SpaceKeeper Vertical - Model “SRV” Guide Specifications

Part 1: General

  - The HVAC system is based on BULLDOG Reversing Heat Pump System.

  - The system will automatically provide the availability of heating or cooling functions 24 hours a day, 365 days a year without need for a changeover.

  - Model selection and performance shall be in accordance with the schedule on the drawings.

  - Mechanical cooling shall be enabled with Entering Condenser Water below 125⁰F.

  - Each unit/chassis shall be pressure tested with Nitrogen on both the refrigerant and fluid (water) circuits followed by a helium leak detection program for both circuits. Units are then attached to the vacuum system for at least 2 hours and monitored.

  - Each unit shall be run tested with a water/ glycol solution to ensure 100% functionality in all modes of operation.

  - Individual units/chassis shall be self-contained and complete when shipped from the factory.

  - Units shall be safety certified and bear a seal of approval from one of UL/ULC/ETL or ESA. All units must be AHRI certified and meet ASHRAE 90.1 minimum standard.

  - Manufacturer shall warrant the parts only of each unit for a period of 12 months from the start-up date or 18 months from the unit shipment date whichever occurs first.

  - Commissioning of the BULLDOG unit(s) shall be performed by a CGC trained technician. A commissioning report shall be provided by the commissioning technician for review and approval by the owner’s representative.

  - It is the contractor’s responsibility to have the system properly flushed and cleaned prior to commissioning.

  - Alternate proposals shall include consideration for equipment space requirements, pipe and equipment sizing, electrical installation impact, operation costs, sound implications and redesign fees.

Part 2: Mechanical Parts

  - Housing

    - The housing of the unit shall be constructed based on a frame and panel principle with removable panels for maximum service access.

    - Painted exterior panels is available on units sized 008 – 060. Painted exterior panels are standard on units sized 070-100.

    - The unit shall be fabricated with heavy gauge steel with all Interior of cabinet lined with 1/2” acoustic insulation.

    - The supply air opening shall be complete with discharge duct collar.

    - The service panels shall be easily removable and sufficiently large to allow access to all components.

  - Blower and Motor

    - The complete blower section including motor shall be easily accessible and removable for service.

    - The blower shall be statically and dynamically balanced.

    - The blower shall be directly driven by an EC motor that has an integral thermal overload protection for units up to size 060.

    - The blower shall be belt driven by a three-phase motor with integral thermal overload protection and equipped with a variable frequency drive (VFD) for unit sized 070 - 100. The belt drive blower motor fan speed shall be adjustable by means of the VFD.

    - The fan motor shall be open drip proof on all direct drive types and shall be totally enclosed fan cooled for belt driven types.

  - Filter

    - The filter chamber shall be an integral part of the system located on return air path and should be serviceable from the front/ rear of the unit.

    - The filter shall be standard capacity, 1 inch thick “Disposable” type shipped with unit sizes 008-060 and 2” MERV 8 standard on sizes 070-100.

*(Optional) MERV 8 (on sizes 008-060) & MERV 13 filters.

*(Optional Ducted Filter Box.

Part 3: Refrigeration Parts

  - Refrigeration System

    - The refrigeration circuit shall be available for operation on non-ozone depleting, low GWP R454B refrigerant.

    - The refrigeration circuit shall have the following components:

- Thermostatic Expansion Valve (TXV) with external equalizer – bi-directional

- Filter dryer – bi-directional

- High pressure cut-out

- High pressure service port

- Low pressure cut-out

- Low pressure service port

- Refrigerant Sight glass (on models 070 and up)

- Reversing valve, sliding piston type pilot operated with a 24 VAC solenoid coil.

*(Optional) Sight Glass on units up to size 060

    - The service ports shall be located to facilitate field service with unit in place.

    - All refrigerant piping shall be of type ACR copper pipe.

    - The refrigerant circuit and components shall be factory assembled in a sealed, leak and performance tested, properly charged system.

    - The sealed refrigerant circuit shall be certified for 600 PSIG working condensing pressure.

  - Compressor

    - The compressor shall be high efficiency sealed hermetic rotary type for sizes 008 – 018 and hermetic scroll type for sizes 020 and above.

*(Optional) sizes 024 – 060 can be ordered with two-stage hermetic scroll compressors.

*(Optional) sizes 070 – 100 can be ordered with tandem scroll set or dual refrigeration circuits

    - The compressor shall be externally isolated on rubber mounts and connected to refrigerant circuit with floating piping to minimize sound transmission.

    - The compressor motor shall have integral thermal overload protection.

    - The Compressor shall be provided with a 5-minute restart delay to avoid compressor short cycling and low-pressure lockout.

  - Air to Refrigerant Heat Exchanger

    - The refrigerant to air heat exchanger shall be aluminum fin and copper tube construction rated to withstand 470 PSI refrigerant working pressure.

    - The coil shall have a maximum face velocity of 500 FPM.

    - A Stainless-Steel insulated condensate drain pan shall be provided under the coil.

    - The units are shipped with an internally mounted trap supplied by the factory.

  - Water to Refrigerant Heat Exchanger

    - The condenser shall be of the brazed plate type that can withstand pressure up to 600 psi. A 20-mesh size strainer should be installed as standard.

    - The connections shall be female pipe thread mounted flush to the cabinet exterior.

*(Optional) Stainless steel braided flexible Supply/ Return 24” hoses are available upon request.

  - Valve Configuration – Factory Installed

    - All units shall be supplied with one 2-way control valve for variable water flow pumping systems. If the system is bottom fed, all units at the top of each riser can be wired for continuous water flow.

*(Optional) Flow limiting device available upon request.

Part 4: Control Systems

  - System

    - The unit shall be complete with a standard microprocessor controlled electronic circuit board.

    - The control panel shall be supplied with individual 24 VAC control transformer.

    - The control panel shall have LED indicators displaying thermostat call, unit operation and alarms.

    - Units with R454B refrigerant charge more than 62.5 oz are equipped with refrigerant leak detector sensor and a board that in case of a leak detection it will disconnect the compressor and run the circulation fan.

    - The control board shall operate with:

- A 24-volt thermostat

- Onboard fuse protection

    - A remote alarm contact is available for connection to alarm monitor by others – monitored and wired by others.

    - BMS override function available to disable compressor only or disable unit. BMS override and wiring by others.

    - Condensate High Level Monitor and alarm is available.

*(Optional) Different types of BULLDOG thermostats are available upon request.

  - Alarms

The standard Control Panel shall have the following standard alarms:

- Low Coil Temperature

- High Leaving Water Temperature

- Low Discharge Air Temperature

- Low Refrigerant Pressure

- High Refrigerant Pressure

- High Condensate Level